{"text_format":"3","workbook":"xlsx","n_sheets":4,"sheets":["1#电梯","2#电梯","3#电梯","4#电梯 "],"read":"whole","date_system":"1900"}

{"sheet":"1#电梯","index":0,"n_rows":48,"n_cols":5,"rows_kept":48,"merged":[[0,2,0,7],[1,0,1,4],[2,0,3,0],[2,3,2,4],[4,1,16,1],[10,3,10,4],[11,3,11,4],[12,3,12,4],[13,3,13,4],[14,3,14,4],[15,3,15,4],[16,3,16,4],[17,1,21,1],[18,3,18,4],[19,3,19,4],[20,3,20,4],[21,3,21,4],[22,1,32,1],[22,3,22,4],[23,3,23,4],[24,3,24,4],[25,3,25,4],[26,3,26,4],[27,3,27,4],[28,3,28,4],[29,3,29,4],[30,3,30,4],[31,3,31,4],[32,3,32,4],[33,1,39,1],[33,3,33,4],[35,3,35,4],[36,3,36,4],[37,3,37,4],[38,3,38,4],[39,3,39,4],[40,1,44,1],[40,3,40,4],[41,3,41,4],[42,3,42,4],[43,3,43,4],[44,3,44,4],[45,1,47,1],[45,3,45,4],[46,3,46,4],[47,3,47,4]]}
["附件1"]
["1#电梯技术规格及装修配置标准"]
["序号","类别","楼号"]
[null,null,"电梯类型"]
[1,"一般要求","配置标准（数量）"]
[2,null,"电梯型号（投标人填报）"]
[3,null,"载重量","1150KG"]
[4,null,"速度","1.0m/s"]
[5,null,"停层",2]
[6,null,"行程","5.27m"]
[7,null,"驱动方式","交流变频变压无级调速无齿拖动系统"]
[8,null,"电源","动力电源：电压：380V 频率：50Hz 相数：3相5线制"]
[9,null,"控制方式","单控"]
[10,null,"曳引机","永磁同步无齿轮曳引机，采用聚氨酷包裹钢丝构成的钢带或曳引媒介，曳引机为投标品牌原厂原品牌（提供原厂原品牌曳引机型式试验报告）"]
[11,null,"对重砣位置","侧置"]
[12,null,"缓冲器","液压缓冲器"]
[13,null,"对重补偿砣","厂家标准"]
[14,"土建要求","井道尺寸（宽*深）mm","2200*2400","基坑2100*2400"]
[15,null,"机房尺寸（宽*深*高）mm","无机房电梯"]
[16,null,"机房高度mm","无机房电梯"]
[17,null,"顶层高度mm",4500]
[18,null,"底坑深度mm",1600]
[19,"轿厢设计","轿厢内尺寸\n（宽*深）","1400*1850"]
[20,null,"轿厢天花型号","LED平板灯+发纹不锈边框"]
[21,null,"轿厢净高",2400]
[22,null,"轿厢前壁","发纹不锈钢"]
[23,null,"轿厢侧壁","发纹不锈钢"]
[24,null,"轿厢后壁","发纹不锈钢"]
[25,null,"轿厢门","发纹不锈钢"]
[26,null,"轿厢地面","拼花PVC耐磨地板"]
[27,null,"扶手","三方扶手"]
[28,null,"护脚板","厂家标准"]
[29,null,"通风形式","低噪音风机通风"]
[30,"电梯门设计","开门方式","中分"]
[31,null,"门宽mm",900]
[32,null,"门高mm",2100]
[33,null,"梯门","每层发纹不锈钢"]
[34,null,"门套","每层发纹不锈钢"]
[35,null,"门坎","铝合金"]
[36,null,"门安全装置","门电机防水防尘等级≥IP65(提供门机试验报告) "]
[37,"轿厢操纵箱及显示器","轿厢控制屏","白色段码显示器，发纹不锈钢"]
[38,null,"面板材质","银丝玻璃面板+发纹不锈钢底板"]
[39,null,"楼层显示器"," 白色段码显示器"]
[40,null,"数字显示"," 白色段码显示器"]
[41,null,"按钮类型","不锈钢盲文按钮"]
[42,"电梯厅控制","面板设计","银丝玻璃面板"]
[43,null,"召唤指示器","白色段码显示"]
[44,null,"呼叫按钮控制","银色圆形按钮"]

{"sheet":"2#电梯","index":1,"n_rows":48,"n_cols":5,"rows_kept":48,"merged":[[0,2,0,7],[1,0,1,4],[2,0,3,0],[2,3,2,4],[4,1,16,1],[10,3,10,4],[11,3,11,4],[12,3,12,4],[13,3,13,4],[14,3,14,4],[15,3,15,4],[16,3,16,4],[17,1,21,1],[18,3,18,4],[19,3,19,4],[20,3,20,4],[21,3,21,4],[22,1,32,1],[22,3,22,4],[23,3,23,4],[24,3,24,4],[25,3,25,4],[26,3,26,4],[27,3,27,4],[28,3,28,4],[29,3,29,4],[30,3,30,4],[31,3,31,4],[32,3,32,4],[33,1,39,1],[33,3,33,4],[35,3,35,4],[36,3,36,4],[37,3,37,4],[38,3,38,4],[39,3,39,4],[40,1,44,1],[40,3,40,4],[41,3,41,4],[42,3,42,4],[43,3,43,4],[44,3,44,4],[45,1,47,1],[45,3,45,4],[46,3,46,4],[47,3,47,4]]}
["附件1"]
["2#电梯技术规格及装修配置标准"]
["序号","类别","楼号"]
[null,null,"电梯类型"]
[1,"一般要求","配置标准（数量）"]
[2,null,"电梯型号（投标人填报）"]
[3,null,"载重量","1150KG"]
[4,null,"速度","1.0m/s"]
[5,null,"停层",2]
[6,null,"行程","8.72m"]
[7,null,"驱动方式","交流变频变压无级调速无齿拖动系统"]
[8,null,"电源","动力电源：电压：380V 频率：50Hz 相数：3相5线制"]
[9,null,"控制方式","单控"]
[10,null,"曳引机","永磁同步无齿轮曳引机，采用聚氨酷包裹钢丝构成的钢带或曳引媒介，曳引机为投标品牌原厂原品牌（提供原厂原品牌曳引机型式试验报告）"]
[11,null,"对重砣位置","侧置"]
[12,null,"缓冲器","液压缓冲器"]
[13,null,"对重补偿砣","厂家标准"]
[14,"土建要求","井道尺寸（宽*深）mm","2000*2200","基坑2000*2100"]
[15,null,"机房尺寸（宽*深*高）mm","无机房电梯"]
[16,null,"机房高度mm","无机房电梯"]
[17,null,"顶层高度mm",4500]
[18,null,"底坑深度mm",1600]
[19,"轿厢设计","轿厢内尺寸\n（宽*深）","1500*1600"]
[20,null,"轿厢天花型号","LED平板灯+发纹不锈边框"]
[21,null,"轿厢净高",2400]
[22,null,"轿厢前壁","发纹不锈钢"]
[23,null,"轿厢侧壁","发纹不锈钢"]
[24,null,"轿厢后壁","发纹不锈钢"]
[25,null,"轿厢门","发纹不锈钢"]
[26,null,"轿厢地面","拼花PVC耐磨地板"]
[27,null,"扶手","三方扶手"]
[28,null,"护脚板","厂家标准"]
[29,null,"通风形式","低噪音风机通风"]
[30,"电梯门设计","开门方式","中分"]
[31,null,"门宽mm",900]
[32,null,"门高mm",2100]
[33,null,"梯门","每层发纹不锈钢"]
[34,null,"门套","每层发纹不锈钢"]
[35,null,"门坎","铝合金"]
[36,null,"门安全装置","门电机防水防尘等级≥IP65(提供门机试验报告) "]
[37,"轿厢操纵箱及显示器","轿厢控制屏","白色段码显示器，发纹不锈钢"]
[38,null,"面板材质","银丝玻璃面板+发纹不锈钢底板"]
[39,null,"楼层显示器"," 白色段码显示器"]
[40,null,"数字显示"," 白色段码显示器"]
[41,null,"按钮类型","不锈钢盲文按钮"]
[42,"电梯厅控制","面板设计","银丝玻璃面板"]
[43,null,"召唤指示器","LED白色段码显示"]
[44,null,"呼叫按钮控制","银色圆形按钮"]

{"sheet":"3#电梯","index":2,"n_rows":48,"n_cols":5,"rows_kept":48,"merged":[[0,2,0,7],[1,0,1,4],[2,0,3,0],[2,3,2,4],[4,1,16,1],[10,3,10,4],[11,3,11,4],[12,3,12,4],[13,3,13,4],[14,3,14,4],[15,3,15,4],[16,3,16,4],[17,1,21,1],[18,3,18,4],[19,3,19,4],[20,3,20,4],[21,3,21,4],[22,1,32,1],[22,3,22,4],[23,3,23,4],[24,3,24,4],[25,3,25,4],[26,3,26,4],[27,3,27,4],[28,3,28,4],[29,3,29,4],[30,3,30,4],[31,3,31,4],[32,3,32,4],[33,1,39,1],[33,3,33,4],[35,3,35,4],[36,3,36,4],[37,3,37,4],[38,3,38,4],[39,3,39,4],[40,1,44,1],[40,3,40,4],[41,3,41,4],[42,3,42,4],[43,3,43,4],[44,3,44,4],[45,1,47,1],[45,3,45,4],[46,3,46,4],[47,3,47,4]]}
["附件1"]
["3#电梯技术规格及装修配置标准"]
["序号","类别","楼号"]
[null,null,"电梯类型"]
[1,"一般要求","配置标准（数量）"]
[2,null,"电梯型号（投标人填报）"]
[3,null,"载重量","1150KG"]
[4,null,"速度","1.0m/s"]
[5,null,"停层",2,"中部增设2个安全门站点"]
[6,null,"行程","24.18m"]
[7,null,"驱动方式","交流变频变压无级调速无齿拖动系统"]
[8,null,"电源","动力电源：电压：380V 频率：50Hz 相数：3相5线制"]
[9,null,"控制方式","单控"]
[10,null,"曳引机","永磁同步无齿轮曳引机，采用聚氨酷包裹钢丝构成的钢带或曳引媒介，曳引机为投标品牌原厂原品牌（提供原厂原品牌曳引机型式试验报告）"]
[11,null,"对重砣位置","侧置"]
[12,null,"缓冲器","液压缓冲器"]
[13,null,"对重补偿砣","厂家标准"]
[14,"土建要求","井道尺寸（宽*深）mm","2000*2200","基坑2000*2100"]
[15,null,"机房尺寸（宽*深*高）mm","无机房电梯"]
[16,null,"机房高度mm","无机房电梯"]
[17,null,"顶层高度mm",4500]
[18,null,"底坑深度mm",1600]
[19,"轿厢设计","轿厢内尺寸\n（宽*深）","1500*1600"]
[20,null,"轿厢天花型号","LED平板灯+发纹不锈边框"]
[21,null,"轿厢净高",2400]
[22,null,"轿厢前壁","发纹不锈钢"]
[23,null,"轿厢侧壁","发纹不锈钢"]
[24,null,"轿厢后壁","发纹不锈钢"]
[25,null,"轿厢门","发纹不锈钢"]
[26,null,"轿厢地面","拼花PVC耐磨地板"]
[27,null,"扶手","三方扶手"]
[28,null,"护脚板","厂家标准"]
[29,null,"通风形式","低噪音风机通风"]
[30,"电梯门设计","开门方式","中分"]
[31,null,"门宽mm",900]
[32,null,"门高mm",2100]
[33,null,"梯门","每层发纹不锈钢"]
[34,null,"门套","每层发纹不锈钢"]
[35,null,"门坎","铝合金"]
[36,null,"门安全装置","门电机防水防尘等级≥IP65(提供门机试验报告) "]
[37,"轿厢控制屏及显示器","轿厢控制屏","LED白色段码显示器，发纹不锈钢"]
[38,null,"面板材质","银丝玻璃面板+发纹不锈钢底板"]
[39,null,"楼层显示器"," 白色段码显示器"]
[40,null,"数字显示"," 白色段码显示器"]
[41,null,"按钮类型","不锈钢盲文按钮"]
[42,"电梯厅控制","面板设计","银丝玻璃面板"]
[43,null,"召唤指示器","LED白色段码显示"]
[44,null,"呼叫按钮控制","银色圆形按钮"]

{"sheet":"4#电梯 ","index":3,"n_rows":48,"n_cols":5,"rows_kept":48,"merged":[[0,2,0,7],[1,0,1,4],[2,0,3,0],[2,3,2,4],[4,1,16,1],[10,3,10,4],[11,3,11,4],[12,3,12,4],[13,3,13,4],[14,3,14,4],[15,3,15,4],[16,3,16,4],[17,1,21,1],[18,3,18,4],[19,3,19,4],[20,3,20,4],[21,3,21,4],[22,1,32,1],[22,3,22,4],[23,3,23,4],[24,3,24,4],[25,3,25,4],[26,3,26,4],[27,3,27,4],[28,3,28,4],[29,3,29,4],[30,3,30,4],[31,3,31,4],[32,3,32,4],[33,1,39,1],[33,3,33,4],[35,3,35,4],[36,3,36,4],[37,3,37,4],[38,3,38,4],[39,3,39,4],[40,1,44,1],[40,3,40,4],[41,3,41,4],[42,3,42,4],[43,3,43,4],[44,3,44,4],[45,1,47,1],[45,3,45,4],[46,3,46,4],[47,3,47,4]]}
["附件1"]
["4#电梯技术规格及装修配置标准"]
["序号","类别","楼号"]
[null,null,"电梯类型"]
[1,"一般要求","配置标准（数量）"]
[2,null,"电梯型号（投标人填报）"]
[3,null,"载重量","1150KG"]
[4,null,"速度","1.0m/s"]
[5,null,"停层",2,"中部增设2个安全门站点"]
[6,null,"行程","26.80m"]
[7,null,"驱动方式","交流变频变压无级调速无齿拖动系统"]
[8,null,"电源","动力电源：电压：380V 频率：50Hz 相数：3相5线制"]
[9,null,"控制方式","单控"]
[10,null,"曳引机","永磁同步无齿轮曳引机，采用聚氨酷包裹钢丝构成的钢带或曳引媒介，曳引机为投标品牌原厂原品牌（提供原厂原品牌曳引机型式试验报告）"]
[11,null,"对重砣位置","侧置"]
[12,null,"缓冲器","液压缓冲器"]
[13,null,"对重补偿砣","厂家标准"]
[14,"土建要求","井道尺寸（宽*深）mm","2200*2400","基坑2100*2400"]
[15,null,"机房尺寸（宽*深*高）mm","无机房电梯"]
[16,null,"机房高度mm","无机房电梯"]
[17,null,"顶层高度mm",4500]
[18,null,"底坑深度mm",1600]
[19,"轿厢设计","轿厢内尺寸\n（宽*深）","1400*1850"]
[20,null,"轿厢天花型号","LED平板灯+发纹不锈边框"]
[21,null,"轿厢净高",2400]
[22,null,"轿厢前壁","发纹不锈钢"]
[23,null,"轿厢侧壁","发纹不锈钢"]
[24,null,"轿厢后壁","发纹不锈钢"]
[25,null,"轿厢门","发纹不锈钢"]
[26,null,"轿厢地面","拼花PVC耐磨地板"]
[27,null,"扶手","三方扶手"]
[28,null,"护脚板","厂家标准"]
[29,null,"通风形式","低噪音风机通风"]
[30,"电梯门设计","开门方式","中分"]
[31,null,"门宽mm",900]
[32,null,"门高mm",2100]
[33,null,"梯门","每层发纹不锈钢"]
[34,null,"门套","每层发纹不锈钢"]
[35,null,"门坎","铝合金"]
[36,null,"门安全装置","门电机防水防尘等级≥IP65(提供门机试验报告)\n"]
[37,"轿厢操纵箱及显示器","轿厢控制屏","LED白色段码显示器，发纹不锈钢"]
[38,null,"面板材质","银丝玻璃面板+发纹不锈钢底板"]
[39,null,"楼层显示器"," 白色段码显示器"]
[40,null,"数字显示"," 白色段码显示器"]
[41,null,"按钮类型","不锈钢盲文按钮"]
[42,"电梯厅控制","面板设计","银丝玻璃面板"]
[43,null,"召唤指示器","LED白色段码显示"]
[44,null,"呼叫按钮控制","银色圆形按钮"]